U.S. Boiler Company

Sage2 Controller

Modbus Interface List

Revision preliminary

December 13, 2012

Document Revision History:

| Date | Description | Author |
| --- | --- | --- |
|  | Preliminary Release |  |

1	Introduction	5

1.1	Definitions	5

1.2	References	5

2	Interface	6

2.1	Physical Layer	6

2.2	Application Layer	6

2.2.1	Register Writes	18

2.2.2	03 (0x03) Read Holding Registers	19

2.2.3	06 (0x06) Write Single Register	19

2.2.4	16 (0x10) Write Multiple Registers	19

2.2.5	17 (0x11) Report Slave ID	20

2.2.6	Exception Codes	20

# Introduction

This document describes the interface to the Integrated Combustion Control Platform (SAGE2) on either the MB1 or MB2 Modbus ports. Each Modbus port is a communications port that allows configuration and status data to be read and written to the SAGE2. These ports are RS-485 connectors that use the Modbus communication protocol for it’s interface.

The SAGE2 functions as a Modbus slave (server) on this interface. It responds to a single Modbus address to service the requests of the Modbus master (client) on the RS-485 network.

This document doesn’t describe the Modbus protocol. It only describes how this protocol is used in this interface.

## Definitions

The following definitions are used in this document:

| SAGE2 | Integrated Combustion Control Platform – internal development name for SAGE2 product. |
| --- | --- |
| Modbus | Application layer communication protocol standard adopted by the Modbus-IDA trade association. Recognized as an industry standard protocol for RS-485 serial communication. |
| PCB | Parameter Control Block. Files that customize the user interface with the SAGE2. PCBs reside in the non-volatile storage in the SAGE2 and are uploaded from the SAGE2 into the user interface. |
| PM | Program Module. Plug that can be inserted into the SAGE2 to enable Lead Lag and to backup & restore parameter settings in the SAGE2. |
| RTU | Remote Terminal Unit serial transmission mode. Mode used to encode data for Modbus where each 8-bit byte is sent as two 4-bit hexadecimal characters. |

## References

The following documents are referenced by this document:

- MODBUS Application Protocol Specification V1.1a, June 4, 2004, http://www.Modbus-IDA.org.

# Interface

## Physical Layer

The SAGE2 Modbus port is a 3-pin connector that interfaces to the following RS-485 signals:

| Signal | Terminal |
| --- | --- |
| Data + (a) | 1 |
| Data – (b) | 2 |
| Common (c) | 3 |

Table 1 RS-485 Signals

Serial transmission mode on the Modbus network is RTU mode. Message format has the following characteristics:

| Coding system | 8-bit binary |
| --- | --- |
| Number of data bits per character | 10 = 1 start bit 8 data bits No parity bit 1 stop bit |
| Bit transfer rate | 38400 bps |
| Duplex | Half duplex |
| Error checking | 2 byte CRC-16 polynomial |
| Bit transfer order | LSB first |
| End of message | Idle line for 3.5 or more characters |

Table 2 RS-485 Message Format

## Application Layer

The SAGE2 Modbus interface supports the following function codes:

- 03 (0x03) Read Holding Registers

- 06 (0x06) Write Single Register

- 16 (0x10) Write Multiple Registers

- 17 (0x11) Report Slave ID

All of the configuration and status data are accessed as 16-bit holding registers in this interface. Since all SAGE2 digital signals accessed in this interface are read only, these digital signals are mapped to bits within holding registers instead of coils or discrete inputs to simplify the interface. Variable length data are also represented by holding registers, and therefore, must be accessed individually and not as part of a group. The length of the variable length data is returned in the response. All 32-bit data items are accessed as two consecutive 16-bit holding registers, i.e., each item uses 2 register address spaces.

The holding register map is defined in the following table. Except for variable length data items the registers can be accessed as a single register or up to 20 registers for writes and 125 registers for reads. Data is mapped into logical groups with room for future expansion so some gaps exist in the register map.

Data organization is intended to allow for efficient register access. Status data is organized into register blocks by application function and a function status change indicator is used to denote when any data has changed within the register block since the last time the registers were read (see the following figure). The SAGE2 sets the status change indicator bit when at least one of the registers in the functional block has changed value since it was last read. The Modbus master can read the status change register and determine which functional register blocks have changed value since it’s last access and only read those register blocks. The Modbus master can ignore the status change register and poll status data as it deems fit.

| Register | Parameter | Read/ Write | Format | Note |
| --- | --- | --- | --- | --- |
| 0007 | Supply sensor | R | U16 | -40°-130° (0.1°C precision) |
| 0008 | Firing rate Commanded | R | U16 | Actual firing rate (% or RPM). |
| 0009 | Fan speed Measured | R | U16 | RPM |
| 0010 | Flame signal | R | U16 | 0.01V or 0.01μA precision (0.00-50.00V) |
| 0011 | Return sensor | R | U16 | -40°-130° (0.1°C precision)1 |
| 0013 | Header sensor | R | U16 | -40°-130° (0.1°C precision)1 |
| 0014 | Stack sensor | R | U16 | -40°-130° (0.1°C precision)1 |
| 0016 | Active CH setpoint | R | U16 | -40°-130° (0.1°C precision)1 Setpoint determined by CH setpoint source (register 65). |
| 0017 | Active DHW setpoint | R | U16 | -40°-130° (0.1°C precision)1 Setpoint determined by DHW setpoint source (register 81). |
| 0018 | Active LL setpoint | R | U16 | -40°-130° (0.1°C precision)1 Setpoint determined by LL setpoint source (register 161). |
| 0025 | Active CH operating point | R | U16 | -40°-130° (0.1°C precision)1 |
| 0026 | Active DHW operating point | R | U16 | -40°-130° (0.1°C precision)1 |
| 0027 | Active Lead Lag operating point | R | U16 | -40°-130° (0.1°C precision)1 |
| 0028 | Active system operating point | R | U16 | -40°-130° (0.1°C precision)1 |
| 0029 | Active system setpoint | R | U16 | -40°-130° (0.1°C precision)1 |
| 0030 | Active system on hysteresis | R | U16 | 0°-130° (0.1°C precision)1 |
| 0031 | Active system off hysteresis | R | U16 | 0°-130° (0.1°C precision)1 |
|  | BURNER CONTROL STATUS |  |  |  |
| 0033 | Burner control state | R | U16 | Burner control sequence (I/O) state (see table 11). Model type determined by register 176. |
| 0034 | Lockout code | R | U16 | 0=No lockout, 1-4096 (see Table 8) |
| 0040 | Hold code | R | U16 | Reason for burner hold (same codes as lockout, see table 7) |
|  | SENSOR STATUS |  |  |  |
| 0048 | Supply sensor (S3=J8-8) state | R | U16 | 0=None, 1=Normal, 2=Open, 3=Shorted, 4=Outside high range, 5=Outside low range, 6=Not reliable |
| 0049 | Return sensor (S1=J8-4) state | R | U16 | 0=None, 1= Normal, 2=Open, 3=Shorted, 4=Outside high range, 5=Outside low range, 6=Not reliable |
| 0051 | Stack sensor (S8=J9-4) state | R | U16 | 0=None, 1= Normal, 2=Open, 3=Shorted, 4=Outside high range, 5=Outside low range, 6=Not reliable |
| 0052 | Header sensor state | R | U16 | 0=None, 1= Normal, 2=Open, 3=Shorted, 4=Outside high range, 5=Outside low range, 6=Not reliable |
| 0053 | 4-20mA remote control input (S2=J8-6) state | R | U16 | 0=None, 1= Normal, 2=Open, 3=Shorted, 4=Outside high range, 5=Outside low range, 6=Not reliable |
|  | DEMAND & MODULATION STATUS |  |  |  |
| 0061 | Active system sensor | R | U16 | Modulation sensor for active priority loop: 0=No active sensor, 1=DHW (S6S7) sensor, 2=Outlet (S3S4) sensor. 3=Inlet (S1) sensor, 4=4-20mA input (S2), 5=S5 sensor, 6=S10 sensor, 7=Steam (S1) sensor |
| 0062 | Active Lead Lag sensor | R | U16 | Active modulation sensor for Lead Lag loop: 0=No active sensor, 2=Outlet (S3S4) sensor, 5=S5 sensor, 6=S10 sensor |
|  | CENTRAL HEATING (CH) STATUS |  |  |  |
| 0065 | CH setpoint source | R | U16 | 0=Unknown, 1=Normal setpoint, 2=TOD setpoint, 3=Outdoor reset, 4=Remote control, 7=Outdoor reset time of day |
| 0066 | CH heat demand | R | U16 | 0=Off, 1=On |
| 0068 | CH requested rate | R | U16 | RPM or %3 |
| 0070 | CH frost burner demand | R | U16 | 0=Off, 1=On |
| 0071 | Active CH on hysteresis | R | U16 | 0°-130° (0.1°C precision)1 |
| 0072 | Active CH off hysteresis | R | U16 | 0°-130° (0.1°C precision)1 |
| 0076 | Active CH sensor | R | U16 | Active modulation sensor for CH loop: 0=No active sensor, 2=Outlet (S3S4) sensor, 3=Inlet (S1) sensor, 4=4-20mA input (S2), 5=S5 sensor, 6=S10 sensor, 7=Steam (S1) sensor |
|  | DOMESTIC HOT WATER (DHW) STATUS |  |  |  |
| 0079 | Active DHW sensor | R | U16 | Active modulation sensor for DHW loop: 0=No active sensor, 1=DHW (S6S7) sensor, 2=Outlet (S3S4) sensor, 3=Inlet (S1) sensor |
| 0081 | DHW setpoint source | R | U16 | 0=Unknown, 1=Normal setpoint, 2=TOD setpoint, 5=DHW tap setpoint, 6=DHW preheat setpoint |
| 0082 | DHW priority count | R | U16 | Countdown of time when DHW has priority over CH (secs). Applicable when DHW priority time is enabled (see register 452). |
| 0083 | DHW heat demand | R | U16 | 0=Off, 1=On |
| 0088 | Active DHW on hysteresis | R | U16 | 0°-130° (0.1°C precision)1 |
| 0089 | Active DHW off hysteresis | R | U16 | 0°-130° (0.1°C precision)1 |
|  | PUMP STATUS |  |  |  |
| 0096 | CH pump status | R | U16 | For application build less than 1600 see table 12. For application build 1600 or higher see table 13. |
| 0100 | DHW pump status | R | U16 | For application build less than 1600 see table 12. For application build 1600 or higher see table 135. |
| 0108 | Boiler pump status | R | U16 | For application build less than 1600 see table 12. For application build 1600 or higher see table 135. |
|  | STATISTICS |  |  |  |
| 0128- 0129 | Burner cycle count | R/W | U32 | 0-999,999 |
| 0130- 0131 | Burner run time | R/W | U32 | Hours |
| 0132- 0133 | CH pump cycle count | R/W | U32 | 0-999,999 |
| 0134- 0135 | DHW pump cycle count | R/W | U32 | 0-999,999 |
| 0138- 0139 | Boiler pump cycle count | R/W | U32 | 0-999,999 |
|  | LEAD LAG STATUS |  |  |  |
| 0162 | Lead Lag master setpoint source | R R | U16 U16 | 0=Unknown, 1=CH setpoint, 2=CH TOD setpoint, 3=Outdoor reset, 4=Remote control (4-20mA or Modbus), 5=DHW setpoint, 6=DHW TOD setpoint, 7=Outdoor reset time of day, 8=Mix setpoint |
| 0164 | Lead Lag slave burner demand | R | U16 | 0=Off, 1=On |
|  | EXTENDED SENSOR STATUS |  |  |  |
| 0170 | Outdoor temperature | R | U16 | -40°-130° (0.1°C precision)1 |
| 0171 | Outdoor sensor state | R | U16 | 0=None, 1= Normal, 2=Open, 3=Shorted, 4=Outside high range, 5=Outside low range, 6=Not reliable |
|  | LOCKOUT HISTORY |  |  |  |
| 0864- 0880 | Lockout history record 1 | R |  | Most recent lockout. See Table 5. |
| 0881- 0897 | Lockout history record 2 | R |  | 2nd newest lockout. See Table 5. |
| 0898- 0914 | Lockout history record 3 | R |  | 3rd newest lockout. See Table 5. |
| 0915- 0931 | Lockout history record 4 | R |  | 4th newest lockout. See Table 5. |
| 0932- 0948 | Lockout history record 5 | R |  | 5th newest lockout. See Table 5. |
| 0949- 0965 | Lockout history record 6 | R |  | 6th newest lockout. See Table 5. |
| 0966- 0982 | Lockout history record 7 | R |  | 7th newest lockout. See Table 5. |
| 0983- 0999 | Lockout history record 8 | R |  | 8th newest lockout. See Table 5. |
| 1000- 1016 | Lockout history record 9 | R |  | 9th newest lockout. See Table 5. |
| 1017- 1033 | Lockout history record 10 | R |  | 10th newest lockout. See Table 5. |
| 1034- 1050 | Lockout history record 11 | R |  | 11th newest lockout. See Table 5. |
| 1051- 1067 | Lockout history record 12 | R |  | 12th newest lockout. See Table 5. |
| 1068- 1084 | Lockout history record 13 | R |  | 13th newest lockout. See Table 5. |
| 1085- 1101 | Lockout history record 14 | R |  | 14th newest lockout. See Table 5. |
| 1102- 1118 | Lockout history record 15 | R |  | Oldest lockout |
| 1119 | Alarm code | R | U16 | Lockout/alert code causing alarm (see register 2). |

Table 3 SAGE2 Modbus Register Map

Each lockout history record has the format described in the following table.

| Byte Offset | Parameter | Read/ Write | Format | Note |
| --- | --- | --- | --- | --- |
| 0-1 | Lockout code | R | U16 | See register 34 (decimal). |
| 2-3 | Annunciator first out | R | U16 | See register 36 (decimal). |
| 4-5 | Burner control state | R | U16 | See register 33 (decimal). |
| 6-7 | Sequence time | R | U16 | See register 37 (decimal). |
| 8-11 | Cycle | R | U32 | See registers 128-129 (decimal). |
| 12-15 | Hours | R | U32 | See registers 130-131 (decimal). |
| 16-17 | I/O | R | U16 | See register 2 (decimal). |
| 18-19 | Annunciator | R | U16 | See register 3 (decimal). |
| 20-21 | Outlet temperature | R | U16 | See register 7 (decimal). |
| 22-23 | Intlet temperature / Steam pressure | R | U16 | See register 11 or 20 (decimal). Data type is dependent on Product type (register 176). |
| 24-25 | DHW temperature | R | U16 | See register 12 (decimal). |
| 26-27 | Outdoor temperature | R | U16 | See register 13 (decimal). |
| 28-29 | Stack temperature | R | U16 | See register 14 (decimal). |
| 30-31 | 4-20mA input | R | U16 | See register 15 (decimal). |
| 32-33 | Fault data | R | U8 | Fault dependent data (U8 x 2). |

Table 4 SAGE2 Lockout History Record

SAGE2 lockout and hold codes are contained in the following table.

| Code | Description | Note |
| --- | --- | --- |
| 0 | None | No lockout/hold |
| 1 | Unconfigured safety data | Lockout |
| 2 | Waiting for safety data verification | Lockout |
| 3 | Internal fault: Hardware fault | Hold |
| 4 | Internal fault: Safety Relay key feedback error | Hold |
| 5 | Internal fault: Unstable power (DCDC) output | Hold |
| 6 | Internal fault: Invalid processor clock | Hold |
| 7 | Internal fault: Safety relay drive error | Hold |
| 8 | Internal fault: Zero crossing not detected | Hold |
| 9 | Internal fault: Flame bias out of range | Hold |
| 10 | Internal fault: Invalid Burner control state | Lockout |
| 11 | Internal fault: Invalid Burner control state flag | Lockout |
| 12 | Internal fault: Safety relay drive cap short | Hold |
| 13 | Internal fault: PII shorted to ILK | Hold / Lockout |
| 14 | Internal fault: HFS shorted to LCI | Hold / Lockout |
| 15 | Internal fault: Safety relay test failed due to feedback ON | Lockout |
| 16 | Internal fault: Safety relay test failed due to safety relay OFF | Lockout |
| 17 | Internal fault: Safety relay test failed due to safety relay not OFF | Lockout |
| 18 | Internal fault: Safety relay test failed due to feedback not ON | Lockout |
| 19 | Internal fault: Safety RAM write | Lockout |
| 20 | Internal fault: Flame ripple and overflow | Hold |
| 21 | Internal fault: Flame number of sample mismatch | Hold |
| 22 | Internal fault: Flame bias out of range | Hold |
| 23 | Internal fault: Bias changed since heating cycle starts | Hold |
| 24 | Internal fault: Spark voltage stuck low or high | Hold |
| 25 | Internal fault: Spark voltage changed too much during flame sensing time | Hold |
| 26 | Internal fault: Static flame ripple | Hold |
| 27 | Internal fault: Flame rod shorted to ground detected | Hold |
| 28 | Internal fault: A/D linearity test fails | Hold |
| 29 | Internal fault: Flame bias cannot be set in range | Hold |
| 30 | Internal fault: Flame bias shorted to adjacent pin | Hold |
| 31 | Internal fault: SLO electronics unknown error | Hold |
| 32 | Internal fault: Safety Key 0 | Lockout |
| 33 | Internal fault: Safety Key 1 | Lockout |
| 34 | Internal fault: Safety Key 2 | Lockout |
| 35 | Internal fault: Safety Key 3 | Lockout |
| 36 | Internal fault: Safety Key 4 | Lockout |
| 37 | Internal fault: Safety Key 5 | Lockout |
| 38 | Internal fault: Safety Key 6 | Lockout |
| 39 | Internal fault: Safety Key 7 | Lockout |
| 40 | Internal fault: Safety Key 8 | Lockout |
| 41 | Internal fault: Safety Key 9 | Lockout |
| 42 | Internal fault: Safety Key 10 | Lockout |
| 43 | Internal fault: Safety Key 11 | Lockout |
| 44 | Internal fault: Safety Key 12 | Lockout |
| 45 | Internal fault: Safety Key 13 | Lockout |
| 46 | Internal fault: Safety Key 14 | Lockout |
| 47 | Flame rod to ground leakage | Hold |
| 48 | Static flame (not flickering) | Hold |
| 49 | 24VAC voltage low/high | Hold |
| 50 | Modulation fault | Hold |
| 51 | Pump fault | Hold |
| 52 | Motor tachometer fault | Hold |
| 53 | AC inputs phase reversed | Lockout |
| 54 | Safety GVT model ID doesn't match application's model ID | Lockout |
| 55 | Application configuration data block CRC errors | Lockout |
| 56-57 | RESERVED |  |
| 58 | Internal fault: HFS shorted to IAS | Lockout |
| 59 | Internal fault: Mux pin shorted | Lockout |
| 60 | Internal fault: HFS shorted to LFS | Lockout |
| 61 | Anti short cycle | Hold |
| 62 | Fan speed not proved | Hold |
| 63 | LCI OFF | Hold |
| 64 | PII OFF | Hold / Lockout |
| 65 | Interrupted Airflow Switch OFF | Hold / Lockout |
| 66 | Interrupted Airflow Switch ON | Hold / Lockout |
| 67 | ILK OFF | Hold / Lockout |
| 68 | ILK ON | Hold / Lockout |
| 69 | Pilot test hold | Hold |
| 70 | Wait for leakage test completion | Hold |
| 71-77 | RESERVED |  |
| 78 | Demand lost in run | Hold |
| 79 | Outlet high limit | Hold / Lockout |
| 80 | DHW high limit | Hold / Lockout |
| 81 | Delta T inlet/outlet limit | Hold / Lockout |
| 82 | Stack limit | Hold / Lockout |
| 83 | Delta T exchanger/outlet limit | Hold / Lockout |
| 84 | Delta T inlet/exchanger limit | Hold / Lockout |
| 85 | Inlet/outlet inversion limit | Hold / Lockout |
| 86 | Exchanger/outlet inversion limit | Hold / Lockout |
| 87 | Inlet/exchanger inversion limit | Hold / Lockout |
| 88 | Outlet T-rise limit | Hold / Lockout |
| 89 | Exchanger T-rise limit | Hold / Lockout |
| 90 | Heat exchanger high limit | Hold / Lockout |
| 91 | Inlet sensor fault | Hold |
| 92 | Outlet sensor fault | Hold |
| 93 | DHW sensor fault | Hold |
| 94 | S2 (J8-6) sensor fault | Hold |
| 95 | Stack sensor fault | Hold |
| 96 | S5 (J8-11) sensor fault | Hold |
| 97 | Internal fault: A2D mismatch | Lockout |
| 98 | Internal fault: Exceeded VSNSR voltage tolerance | Lockout |
| 99 | Internal fault: Exceeded 28V voltage tolerance | Lockout |
| 100 | Pressure sensor fault | Hold |
| 101-104 | RESERVED |  |
| 105 | Flame detected out of sequence | Hold / Lockout |
| 106 | Flame lost in MFEP | Lockout |
| 107 | Flame lost early in run | Lockout |
| 108 | Flame lost in run | Lockout |
| 109 | Ignition failed | Lockout |
| 110 | Ignition failure occurred | Hold |
| 111 | Flame current lower than WEAK threshold | Hold |
| 112 | Pilot test flame timeout | Lockout |
| 113 | Flame circuit timeout | Lockout |
| 114-121 | RESERVED |  |
| 122 | Lightoff rate proving failed | Lockout |
| 123 | Purge rate proving failed | Lockout |
| 124 | High fire switch OFF | Hold |
| 125 | High fire switch stuck ON | Hold |
| 126 | Low fire switch OFF | Hold |
| 127 | Low fire switch stuck ON | Hold |
| 128 | Fan speed failed during prepurge | Hold / Lockout |
| 129 | Fan speed failed during preignition | Hold / Lockout |
| 130 | Fan speed failed during ignition | Hold / Lockout |
| 131 | Fan movement detected during standby | Hold |
| 132 | Fan speed failed during run | Hold |
| 133-135 | RESERVED |  |
| 136 | Interrupted Airflow Switch failed to close | Hold |
| 137 | ILK failed to close | Hold |
| 138-142 | RESERVED |  |
| 143 | Internal fault: Flame bias out of range 1 | Lockout |
| 144 | Internal fault: Flame bias out of range 2 | Lockout |
| 145 | Internal fault: Flame bias out of range 3 | Lockout |
| 146 | Internal fault: Flame bias out of range 4 | Lockout |
| 147 | Internal fault: Flame bias out of range 5 | Lockout |
| 148 | Internal fault: Flame bias out of range 6 | Lockout |
| 149 | Flame detected | Hold / Lockout |
| 150 | Flame not detected | Hold |
| 151 | High fire switch ON | Hold / Lockout |
| 152 | Combustion pressure ON | Hold / Lockout |
| 153 | Combustion pressure OFF | Hold / Lockout |
| 154 | Purge fan switch ON | Hold / Lockout |
| 155 | Purge fan switch OFF | Hold / Lockout |
| 156 | Combustion pressure and Flame ON | Hold / Lockout |
| 157 | Combustion pressure and Flame OFF | Lockout |
| 158 | Main valve ON | Lockout |
| 159 | Main valve OFF | Lockout |
| 160 | Ignition ON | Lockout |
| 161 | Ignition OFF | Lockout |
| 162 | Pilot valve ON | Lockout |
| 163 | Pilot valve OFF | Lockout |
| 164 | Block intake ON | Lockout |
| 165 | Block intake OFF | Lockout |
| 166-171 | RESERVED |  |
| 172 | Main relay feedback incorrect | Lockout |
| 173 | Pilot relay feedback incorrect | Lockout |
| 174 | Safety relay feedback incorrect | Lockout |
| 175 | Safety relay open | Lockout |
| 176 | Main relay ON at safe start check | Lockout |
| 177 | Pilot relay ON at safe start check | Lockout |
| 178 | Safety relay ON at safe start check | Lockout |
| 179-183 | RESERVED |  |
| 184 | Invalid BLOWER/HSI output setting | Lockout |
| 185 | Invalid Delta T limit enable setting | Lockout |
| 186 | Invalid Delta T limit response setting | Lockout |
| 187 | Invalid DHW high limit enable setting | Lockout |
| 188 | Invalid DHW high limit response setting | Lockout |
| 189 | Invalid Flame sensor type setting | Lockout |
| 190 | Invalid interrupted air switch enable setting | Lockout |
| 191 | Invalid interrupted air switch start check enable setting | Lockout |
| 192 | Invalid Igniter on during setting | Lockout |
| 193 | Invalid Ignite failure delay setting | Lockout |
| 194 | Invalid Ignite failure response setting | Lockout |
| 195 | Invalid Ignite failure retries setting | Lockout |
| 196 | Invalid Ignition source setting | Lockout |
| 197 | Invalid Interlock open response setting | Lockout |
| 198 | Invalid Interlock start check setting | Lockout |
| 199 | Invalid LCI enable setting | Lockout |
| 200 | Invalid lightoff rate setting | Lockout |
| 201 | Invalid Lightoff rate proving setting | Lockout |
| 202 | Invalid Main Flame Establishing Period time setting | Lockout |
| 203 | Invalid MFEP flame failure response setting | Lockout |
| 204 | Invalid NTC sensor type setting | Lockout |
| 205 | Invalid Outlet high limit response setting | Lockout |
| 206 | Invalid Pilot Flame Establishing Period setting | Lockout |
| 207 | Invalid PII enable setting | Lockout |
| 208 | Invalid pilot test hold setting | Lockout |
| 209 | Invalid Pilot type setting | Lockout |
| 210 | Invalid Postpurge time setting | Lockout |
| 211 | Invalid Power up with lockout setting | Lockout |
| 212 | Invalid Preignition time setting | Lockout |
| 213 | Invalid Prepurge rate setting | Lockout |
| 214 | Invalid Prepurge time setting | Lockout |
| 215 | Invalid Purge rate proving setting | Lockout |
| 216 | Invalid Run flame failure response setting | Lockout |
| 217 | Invalid Run stabilization time setting | Lockout |
| 218 | Invalid Stack limit enable setting | Lockout |
| 219 | Invalid Stack limit response setting | Lockout |
| 220 | Unconfigured Delta T limit setpoint setting | Lockout |
| 221 | Unconfigured DHW high limit setpoint setting | Lockout |
| 222 | Unconfigured Outlet high limit setpoint setting | Lockout |
| 223 | Unconfigured Stack limit setpoint setting | Lockout |
| 224 | Invalid DHW demand source setting | Lockout |
| 225 | Invalid Flame threshold setting | Lockout |
| 226 | Invalid Outlet high limit setpoint setting | Lockout |
| 227 | Invalid DHW high limit setpoint setting | Lockout |
| 228 | Invalid Stack limit setpoint setting | Lockout |
| 229 | Invalid Modulation output setting | Lockout |
| 230 | Invalid CH demand source setting | Lockout |
| 231 | Invalid Delta T limit delay setting | Lockout |
| 232 | Invalid Pressure sensor type setting | Lockout |
| 233 | Invalid IAS closed response setting | Lockout |
| 234 | Invalid Outlet high limit enable setting | Lockout |
| 235 | Invalid Outlet connector type setting | Lockout |
| 236 | Invalid Inlet connector type setting | Lockout |
| 237 | Invalid DHW connector type setting | Lockout |
| 238 | Invalid Stack connector type setting | Lockout |
| 239 | Invalid S2 (J8-6) connector type setting | Lockout |
| 240 | Invalid S5 (J8-11) connector type setting | Lockout |
| 241 | Exchanger sensor not allowed with stack connector setting | Lockout |
| 242 | Invalid DHW auto detect configuration | Lockout |
| 243 | Invalid UV with spark interference not compatible with Ignitor on throughout PFEP | Lockout |
| 244 | Internal fault: Safety relay test invalid state | Lockout |
| 245 | Invalid Outlet connector type setting for T-rise | Lockout |
| 246 | 4-20mA cannot be used for both modulation and setpoint control | Lockout |
| 247 | Invalid ILK bounce detection enable | Lockout |
| 248 | Invalid forced recycle interval | Lockout |
| 249 | STAT cannot be demand source when Remote Stat is enabled | Lockout |
| 250 | Invalid Fan speed error response | Lockout |
| 251 | Lead drop-stage on error setting does not match drop method configuration | Lockout |
| 252-255 | RESERVED |  |

Table 5 SAGE2 Lockout/Hold Codes

Burner control states are contained in the following table.

| State | Name |
| --- | --- |
| 0 | Initiate |
| 1 | Standby Delay |
| 2 | Standby |
| 3 | Safe Startup |
| 4 | Prepurge - Drive to Purge Rate |
| 5 | Prepurge – Measured Purge Time |
| 6 | Prepurge – Drive to Lightoff Rate |
| 7 | Preignition Test |
| 8 | Preignition Time |
| 9 | Pilot Flame Establishing Period |
| 10 | Main Flame Establishing Period |
| 11 | Direct Burner Ignition |
| 12 | Run |
| 13 | Postpurge |
| 14 | Lockout |
| 255 | Safety Processor Offline |

Table 6 Burner Control States

SAGE2 pump status codes are contained in the following two tables. The first table is for older SAGE2’s (application build less than 1600), and the second table is for newer SAGE2’s (application build 1600 or higher).

| Status | Description | Note |
| --- | --- | --- |
| 0 | Unknown |  |
| 1 | Not connected |  |
| 2 | Not Lead Lag master |  |
| 3 | Pump A Off |  |
| 4 | Pump B Off |  |
| 5 | Pump C Off |  |
| 6 | Pump A Off – Anti-condensation (CH demand) |  |
| 7 | Pump B Off – Anti-condensation (CH demand) |  |
| 8 | Pump C Off – Anti-condensation (CH demand) |  |
| 9 | Pump A Off – Anti-condensation (DHW demand) |  |
| 10 | Pump B Off – Anti-condensation (DHW demand) |  |
| 11 | Pump C Off – Anti-condensation (DHW demand) |  |
| 12 | Pump A Off – Anti-condensation (LL demand) |  |
| 13 | Pump B Off – Anti-condensation (LL demand) |  |
| 14 | Pump C Off – Anti-condensation (LL demand) |  |
| 15 | Pump A On – Slave overrun |  |
| 16 | Pump B On – Slave overrun |  |
| 17 | Pump C On – Slave overrun |  |
| 18 | Pump A On – LL master overrun |  |
| 19 | Pump B On – LL master overrun |  |
| 20 | Pump C On – LL master overrun |  |
| 21 | Pump A Off – Start delay (DHW demand) |  |
| 22 | Pump B Off – Start delay (DHW demand) |  |
| 23 | Pump C Off – Start delay (DHW demand) |  |
| 24 | Pump A On – CH demand |  |
| 25 | Pump B On – CH demand |  |
| 26 | Pump C On – CH demand |  |
| 27 | Pump A On – CH frost protection |  |
| 28 | Pump B On – CH frost protection |  |
| 29 | Pump C On – CH frost protection |  |
| 30 | Pump A On – DHW demand |  |
| 31 | Pump B On – DHW demand |  |
| 32 | Pump C On – DHW demand |  |
| 33 | Pump A On – DHW frost protection |  |
| 34 | Pump B On – DHW frost protection |  |
| 35 | Pump C On – DHW frost protection |  |
| 36 | Pump A Off – DHW high limit |  |
| 37 | Pump B Off – DHW high limit |  |
| 38 | Pump C Off – DHW high limit |  |
| 39 | Pump A On – Exercise |  |
| 40 | Pump B On – Exercise |  |
| 41 | Pump C On – Exercise |  |
| 42 | Pump A On – Frost protection |  |
| 43 | Pump B On – Frost protection |  |
| 44 | Pump C On – Frost protection |  |
| 45 | Pump A On – Lead Lag master demand |  |
| 46 | Pump B On – Lead Lag master demand |  |
| 47 | Pump C On – Lead Lag master demand |  |
| 48 | Pump A On – Slave demand |  |
| 49 | Pump B On – Slave demand |  |
| 50 | Pump C On – Slave demand |  |
| 51 | Pump A On – Manual |  |
| 52 | Pump B On – Manual |  |
| 53 | Pump C On – Manual |  |
| 54 | Pump A On – Outlet high limit |  |
| 55 | Pump B On – Outlet high limit |  |
| 56 | Pump C On – Outlet high limit |  |
| 57 | Pump A On – Overrun |  |
| 58 | Pump B On – Overrun |  |
| 59 | Pump C On – Overrun |  |
| 60 | Pump A On – Frost protection overrun |  |
| 61 | Pump B On – Frost protection overrun |  |
| 62 | Pump C On – Frost protection overrun |  |
| 63 | Pump A On – Mix demand |  |
| 64 | Pump B On – Mix demand |  |
| 65 | Pump C On – Mix demand |  |

Table 7 Pump Status Codes (Application build less than 1600)

| Status | Description | Note |
| --- | --- | --- |
| 92 | Forced On from manual pump control |  |
| 93 | Forced On due to Outlet high limit is active |  |
| 94 | Forced On from burner demand |  |
| 95 | Forced On due to Lead Lag slave has demand |  |
| 96 | Forced Off from local DHW priority service |  |
| 97 | Forced Off from Lead Lag DHW priority service |  |
| 98 | Forced Off from Central Heat anti-condensation |  |
| 99 | Forced Off from DHW anti-condensation |  |
| 100 | Forced Off due to DHW high limit is active |  |
| 101 | Forced Off from EnviraCOM DHW priority service |  |
| 102 | On due to local CH frost protection is active |  |
| 103 | On due to Lead Lag CH frost protection is active |  |
| 104 | On due to local DHW frost protection is active |  |
| 105 | On due to Lead Lag DHW frost protection is active |  |
| 106 | On from local Central Heat demand |  |
| 107 | On from Lead Lag Central Heat demand |  |
| 108 | On from local DHW demand |  |
| 109 | On from Lead Lag DHW demand |  |
| 110 | On from local Mix demand |  |
| 111 | On from Lead Lag Mix demand |  |
| 112 | On from local Central Heat service |  |
| 113 | On from Lead Lag Central Heat service |  |
| 114 | On from local DHW service |  |
| 115 | On from Lead Lag DHW service |  |
| 116 | On from local Mix service |  |
| 117 | On from Lead Lag Mix service |  |
| 118 | On from Lead Lag auxiliary pump X |  |
| 119 | On from Lead Lag auxiliary pump Y |  |
| 120 | On from Lead Lag auxiliary pump Z |  |
| 121 | On, but inhibited by pump start delay |  |
| 122 | On from pump override |  |
| 123 | Off, not needed |  |
| 124 | On from burner demand |  |
| 125 | On from exercise |  |
| 126 | On from local Lead Lag service |  |
| 127 | On from local Lead Lag pump demand |  |

Table 8 Pump Status Codes (Application build 1600 or higher)

Some holding registers contain variable length data in them, e.g., register 0x00BA (OS number), that extend common Modbus access for holding registers. Only a single register address is assigned to these parameters even though they may contain more than two bytes (16-bits) of data. These registers MUST be accessed individually ONLY in order that no confusion exists about parameter boundaries.

### Register Writes

Writing to any data register may require an access level password before they can be changed (written) by the Modbus master. For those data registers requiring access security a password matching the one contained in the SAGE2 must be provided before the SAGE2 allows the data to be changed. A valid password login remains in effect for 10 minutes before another login is required (SAGE2 timeout for password login). See User Interface Data Attribute Table section for more information regarding how access security is determined.

Two Modbus registers are defined to manage the register data access login:

- (0x00B1) Password

- (0x0013) Register Access Status

The Modbus master writes a password into the Password register to request write access privileges to the data registers. Even though this register is a holding register, and therefore, should normally only accept a 16-bit value, it accepts alphanumeric text up to 20 characters in length. Due to this length change this register must be written individually and not as part of a group register write.

Results of the login are reported by the SAGE2 in the Register Access Status register. If the Modbus master writes the correct installer password, the status register indicates this result and all data with installer access level and below can be changed. If the Modbus master writes the correct OEM password, the status register indicates this result and all data with OEM access level and below can be changed.

### 03 (0x03) Read Holding Registers

This function is used to read one or more consecutive data registers in the SAGE2. The register address of the first register (see Modbus register map in Figure 1) in the range is included in the request along with the number of registers to read. SAGE2 returns a response with the starting register address, the number of bytes returned, followed by the register data contents in register address order (lowest register address first, etc.).

Normally, the number of bytes returned is 2 times the number of registers requested since each register usually contains a 16-bit value. An exception to this rule is that registers representing variable length text data return the length of the text data which can exceed 2 bytes.

### 06 (0x06) Write Single Register

This function is used to write data to a single register in the SAGE2. The SAGE2 register address and 16-bit data value to write into the register are sent to the SAGE2, and the SAGE2 returns an acknowledged response.

Note: This function (command) cannot be used for variable length text data registers.

### 16 (0x10) Write Multiple Registers

This function is used to write data into multiple SAGE2 registers with a single request. The SAGE2 registers must be located consecutively in the register map since only a base address is provided. The Modbus master provides the starting register address, the number of registers to write, the total number of bytes, followed by the actual data itself. The SAGE2 writes the data into each register and acknowledges the completion with a response echoing the number of registers written.

When writing text data to a register representing variable length text, the number of registers should be specified as one and the byte count be the number of bytes in the text data.

### 17 (0x11) Report Slave ID

This function is used to locate and identify the SAGE2s connected on the Modbus network. The Modbus master issues a Report Slave ID request for a specific Modbus address onto the Modbus network, and if an SAGE2 exists with the requested Modbus address, it responds to the request. If no SAGE2 exists, the Modbus master times out and concludes that no SAGE2 is present with that Modbus address.

Included in the SAGE2 response is the following data to further identify it:

- OS number

- Burner name

Format of the SAGE2 response message is depicted in the following table.

| Byte: 0 | 1 | 2 | 3 | 4 | 5-20 | 21-40 | 41-42 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Slave Address | Function Code | Byte Count | Slave ID | Run Indicator | OS Number | Burner Name | CRC |
| 0x01- 0xF0 | 0x11 | 0x30 | 0x79 | 0x00=OFF 0xFF=ON |  |  |  |

Table 9 Report Slave ID Response

The OS number (up to 16 characters) and burner name (up to 20 characters) fields are NULL filled text strings. They have a fixed field length so that the boundaries of each field are known. These same SAGE2 parameters can be obtained with the Read Holding Register function.

The Run Indicator status contains an OFF status when the SAGE2 is in a lockout or unconfigured state. In any other case the status indicates an ON condition.

Note: A slave ID of 0x79 is reserved for all SAGE2 hydronic boiler control models at this time. Future design may expand this list to include more IDs for different models.

### Exception Codes

The Modbus exception codes in the following table may be given by the SAGE2 in response to function code requests.

| Code | Name | Comment |
| --- | --- | --- |
| 0x01 | ILLEGAL_FUNCTION | Illegal function code or action requested |
| 0x02 | ILLEGAL_DATA_ADDRESS | Register address out of bounds |
| 0x03 | ILLEGAL_DATA_VALUE | Data in register write is invalid for register |
| 0x10 | READ_MULTIPLE_NOT_OK | Exceeded maximum registers allowed in read |
| 0x11 | ACCESS_FAILURE | Invalid password access level for register |
| 0x12 | LOGIN_FAILURE | Unrecognized password given for login |

Table 10 Modbus exception codes

## 41000 Registers

To support displays and devices require particular data formats, such as the Panasonic display being developed for Burnham products, a range of virtual registers are implemented with variant data formats.

The range 10000 through 19999 are virtual registers that are mapped onto the base range of 0 through 9999, where all registers in the base range are also accessible in this new range.

The registers in the virtual range behave identically to those in the base range with the following exceptions.

### Temperature

Reading a temperature register in the virtual range provides the temperature in full degrees C or F with rounding up when >= 0.5 degrees (this rounding matches the rounding done in the S7999).  The Temperature units parameter (register 178) determines if F or is C conversion is done.

Writing a temperature register in the virtual range converts the input from degrees C or F to the SOLA internal format of 0.1 degrees C.

### Degrees

Reading a degrees register in the virtual range provides the degrees in full degrees C or F with rounding up when >= 0.5 degrees (this rounding matches the rounding done in the S7999).  The Temperature units parameter (register 178) determines if F or is C conversion is done.

Writing a degrees register in the virtual range converts the input from degrees C or F to the SOLA internal format of 0.1 degrees C.

### Double-word registers (32 bits)

For both reads and writes, the data order is reversed: in the base range the most significant word is at the lower register address whereas in the virtual range the least significant word is at the lower register address.

The cycles and hours within the lockout history are not word order corrected.  You can read just the second register and get a 16 bit value which will be correct until it exceeds 65535 counts or hours (not the 99,000 you stated) at which time it will wrap back to zero.  My comment in the code states lockout history cycle and hours are not used by Burnham’s display and are not translated to conserve code space.

All temperature registers are expressed in °C regardless what Temperature units (register 179) is set to. Temperature range is -40°C to 130°C with values given in 0.1°C units (for example, 32.0°C = 320). A temperature that is NOT applicable in this SAGE2, i.e., not enabled, has a value of 0x8FFF. This temperature setting is denoted as “UNCONFIGURED” at the user interface.

All percentage values are given in 0.1% granularity, i.e., 0-1000 is the range for 0.0-100.0%.

Most significant bit in value determines which units type the parameter has: 0=RPM, 1=%. If Modulation Output parameter (register 192) doesn’t match with the setting of this bit, then the parameter setting is invalid.

Pump control changed in SOLA starting with application build 1600 (see register 189). Pump status changed as a result. Table 12 contains the status values for SOLA prior to build 1600, and table 13 for SOLA that are build 1600 or later.

Standard Modbus protocol doesn’t support the concept of variable length data. The SAGE2 Modbus interface varies from the protocol in that it supports a single register definition for text data. These special registers must be accessed exclusively by themselves in order for them to be supported.